## Main
|  |  |  | Project: | Hospitality Center |  |  | IBC Referenced Standards for Quick Reference:
|  |  |  | Proj #: | ### |  |  | IBC 2012 | IBC 2015 | IBC 2018
|  |  |  | Engineer: | Matt Kantner + Josh Hatfield |  |  | ASCE 7-10 | ASCE 7-10 | ASCE 7-16
|  |  |  | Date: | 2018-03-13 |  |  | AISC 360-10 | AISC 360-10 | AISC 360-16
1) Codes | [7 empty] | AISC 341-10 | AISC 341-10 | AISC 341-16
| Florida Building Code 2017 |  | AISC 360-10 |  | ACI 530-13 |  |  | AISI S100-07/SI-10 | AISI S100-12 | AISI S100-16
| ASCE 7-10 |  | ACI 318-14 |  | NDS 2015 |  |  | ACI 318-11 | ACI 318-14 | ACI 318-14
[8 empty] | ACI 530-11 | ACI 530-13 | TMS 402-2016
[8 empty] | NDS 2012 | NDS 2015 | NDS 2018
2) Building Description
# of Elevated Floors: | 3 + Roof
Roof Type: | Flat
Structural System(s): | Light frame walls, wooden truss floors
Construction Type: | VA
Risk Category: | II
Coordinates: | 47.698 | °N | 116.797 | °W
3) Dead Loads
Typical Floor
Floor Finish (per interiors) |  | 3 | psf | unsure material… 3 psf should be conserv.
1" gypcrete |  | 9 | psf | per ASCE 7-10 Table C.3-1
USG levelrock sound attenuation mat |  | 0.2 | psf | per their website
23/32 plywood (@ 0.4psf per 1/8") |  | 2.4 | psf | per ASCE 7-10 Table C.3-1
Wood trusses |  | 3 | psf | per Mitek
Hanging assembly for ceiling |  | 2 | psf | per ASCE 7-10 Table C.3-1
5/8" gyp ceiling |  | 2.75 | psf | per ASCE 7-10 Table C.3-1
Ducts and lights |  | 3 | psf
Sprinklers |  | 2 | psf | per Mitek, full 2" pipe = 5.13 plf
Extra extra |  | 2.65 | psf
Total |  | 30 | psf
Flat Roof
| Design Roof Loads |  |  | Reliable Roof Loads
Standing Seam Metal Roof (Englert website) |  | 1.3 | psf |  |  | 0.7 | psf
Vapor Barrier |  | 0.1 | psf |  |  | 0 | psf
5/8" sheathing (@ 0.4 psf per 1/8") |  | 2 | psf |  |  | 2 | psf
Wood truss w/ insulation (160+0 /36'x2') |  | 3 | psf |  |  | 2.2 | psf
Ceiling haging eqip |  | 2 | psf |  |  | 1 | psf
Ceiling - 5/8" gyp |  | 2.75 | psf |  |  | 2.75 | psf
Ducts and lights |  | 3 | psf |  |  | 0.35 | psf
Sprinklers |  | 2 | psf |  |  | 1 | psf
Extra extra |  | 8.85 | psf |  |  | 0 | psf
Total |  | 25 | psf | Total |  | 10 | psf
Exterior Walls
2x6 studs at 24 |  | 1.1 | psf
Blocking, top and bottom plates, etc. |  | 1.4 | psf
2 x 5/8" GWB |  | 5.5 | psf
6" batt insulation |  | 0.25 | psf
Rigid insulation (2" @1.5 psf/in) |  | 3 | psf
3/8" wood siding |  | 1.1 | psf
Extra extra |  | 0.65 | psf
Total |  | 13 | psf
4) Live Loads
Second Floor | 40 psf + 15 psf partitions |  |  | Reducible (except partitions)
Roof | 20 psf |  |  | Reducible - Roof
Stairs | 100 psf |  |  | Non-Reducible
5) Wind Loads
Risk Category: | II | [6 empty] | http://windspeed.atcouncil.org/
Exposure Category: | C
Mean Roof Height (ft): | 38.5
Vult (mph): | 149
Vasd (mph): | 117.7948
Gcpi (+/-) | 0.18
6) Seismic Loads | [7 empty] | https://earthquake.usgs.gov/designmaps/us/application.php
N/A
7) Snow Loads
N/A
8) Geotech Criteria
Geotech Report: | Geotechnical Report: Hospitality Center, Kootenai Health Campus
by Strata, In. dated April 12, 2018
|  |  |  | Active Pressure, Ka (psf/ft): |  |  | 35
Allowable bearing (psf): |  | 3000 (3900 W/EQ) |  | At-Rest Pressure, K0 (psf/ft): |  |  | 50
Minimum Footing Dimension (in): |  | 18 |  | Passive Pressure, Kp (psf/ft): |  |  | 400
Sliding Coefficient: |  | 0.45
Frost Protection Depth (in): |  | 24"
SOG Base recommendation: |  | 4" Crushed Aggregate Base
SOG Vapor Barrier Recommendation: |  | yes
Note on B24: Refer to ASCE 7-10 Table C3-1 (p 399)
Note on F40: For use in uplift combos
Note on B63: If goverened by IBC 2015, see Table 1607.1
Note on B71: ASCE 7-10 26.7.3
Note on B72: ASCE 7-10 26.2
Note on B73: ASCE 7-10 Figure 26.5-1A (or 1B or 1C)
Note on B78: ASCE 7-10 Ch 11 Also see link to right

## data
Roof Types | Constr. Type | Exp Cats | Site Class | Seismic Design Cat | Risk Cat | Ie | Is
Flat | 1A | B | A | A | I | 1 | 0.8
Gabled | 1B | C | B | B | II | 1 | 1
Hip | IIA | D | C | C | III | 1.25 | 1.1
Sawtooth | IIB |  | D | D | IV | 1.5 | 1.2
Other | IIIA |  | E | E
| IIIB |  | F | F
IV
VA
VB